## Sheet1
Improvement Plan - DWQMP
IP action # | Source of improvement action (e.g. risk register, audits, incidents etc) | Proposed Treatments or Actions | Priority | Responsibility (position/team) | Timeframe (Original Target) | Revised Timeframe (for delays etc)2 | Status
WQ 1 | Risk Register ID: R1, R17 | Enhance guidance (steps to take) on how to deal with water quality incidents (e.g. E. coli) in the DWQMP. | High | Utilities Engineer | 2023-08-01 |  | Completed
WQ 2 | Risk Register ID: R1 | Discuss with UU to review and modify notification triggers in place for PBPL as a key customer, including around water quality (e.g. include notifications on low total chlorine/monochloramine <0.5 mg/L, low pH <7, high turbidity >1 NTU, ammonia >0.2 mg/L, breaches of aesthetic and health values for initial result etc). This will aid PBPL to undertake any corrective actions or prep/be on alert in case a water quality incident develops. This action will need UU to sample the water delivered to PBPL at appropriate locations (e.g. head meters, when the handover points are reviewed and clear). PBPL to discuss this with UU. | High | Utilities Engineer | 2023-12-01 |  | Completed
WQ 3 | Risk Register ID: R1, R8 | Investigate possibility of establishing a water supply agreement (including communication and triggers around water quality) with UU; or establishing a Memorandum of Understanding (MoU) with UU on notifications and early warning alerts related to water quality from the incoming supply Reservoirs/Zones (e.g. where chlorine is below 0.5 mg/L, ammonia elevates to >0.2 mg/L, regulator notification for incident or event, etc). This will assist PBPL to be on alert and take any relevant actions on their side as possible and practical. | High | Utilities Engineer with relevant PBPL staff and Legal team | 2024-06-01 |  | Completed
WQ 4 | Risk Register ID: R1 | Discuss with UU on the possibility of attending their upcoming water quality related incident and emergency response plan testing/excercise as observers. This will help with maintaining the relationship with UU, give PBPL confidence that the bulk provider is able to manage incidents in a timely manner and will provide PBPL the opportunity to identify any gaps which they may need to improve on their end in regards to incident management. | Medium | Utilities Engineer | 2023-12-01 |  | Completed
WQ 5 | Risk Register ID: R3 | Test or exercise (scenario-based) the BCP and Critical Incident Plan (CIP) with internal stakeholders in relation to a water supply failure (water loss) event. Based on findings from the exercise, update the BCP and ICP, as necessary. | High | Utilities Engineer with relevant PBPL staff | 2024-06-01 | 2026-06-01 | In Progress
WQ 6 | Risk Register ID: R3 | Develop a water supply contingency plan, as needed (based on findings from the exercise), including how much water will be needed, which businesses could remain open with an alternative supply, alternative supplies, contractors/suppliers needed and contacts, customer communications, water restrictions imposed during the event, recovery plan e.g. flushing the network, water testing, etc. | High | Utilities Engineer with relevant PBPL staff | 2024-12-01 | 2026-06-01 | In Progress
WQ 7 | Risk Register ID: R3 | Investigate benefit in having storage tanks/reservoirs on Fisherman Island for supply continuity and resilience. | High | Utilities Engineer | 2025-12-01 | 2025-12-01 | In Progress
WQ 8 | Risk Register ID: R4, R5 | Spread testing of chlorine, turbidity, pH across the network and increase the frequency to weekly (from quarterly). The results for chlorine and turbidity can be used to guide reactive flushing. | High | Utilities Engineer | 2023-12-01 |  | Completed
WQ 9 | Risk Register ID: R5 | Investigate long-term solution for maintaining adequate level of chlorine in the network, that is, rechlorination in the PBPL network. | Medium | Utilities Engineer | 2025-12-01 | 2025-12-01 | On-Hold
WQ 10 | Risk Register ID: R6 | Re-locate the sampling points/taps to the property meter instead of inside the building. | High | Utilities Engineer | 2023-12-01 |  | Completed
WQ 11 | Risk Register ID: R8 | Investigate possibility of chlorinating the network if required (breakpoint, temporary vs permanent, ideal location for it, can it be done by the maintenance contractor if needed, etc). | Medium | Utilities Engineer with relevant PBPL staff | 2025-12-01 | 2025-12-01 | On-Hold
WQ 12 | Risk Register ID: R9 | Undertake a proper condition assessment of whole network. | Medium | Utilities Engineer with relevant PBPL staff | 2024-12-01 |  | Completed
WQ 13 | Risk Register ID: R10 | Review installations process to ensure that it has necessary provisions around water quality (e.g. new water assets/fittings are appropriately disinfected, flushing is undertaken after installation, water quality is tested and has passed). | Medium | Utilities Engineer with relevant PBPL staff | 2024-06-01 |  | Completed
WQ 14 | Risk Register ID: R10, R18 | Develop a contractor awareness/training package for working on PBPL water assets, which includes the DWQMP and implications. | High | Utilities Engineer | 2024-06-01 |  | Completed
WQ 15 | Risk Register ID: R10, R15 | Review the maintenance contract to include a clause on hygienic work practices when working on water assets, including separation/disinfection of tools and equipment. Also include the need for the contractor to ensure that materials used comply with AS4020 or have a WaterMark. | Medium | Utilities Engineer with relevant PBPL staff | 2024-06-01 |  | Completed
WQ 16 | Risk Register ID: R10 | Review the contractors procedure on repair of water mains/pipes to ensure that it has the necessary provisions around water quality (e.g. after repairs there is flushing and water quality testing e.g. turbidity/total chlorine - turbidity should be <1 NTU or not greater than the reading taken just upstream of the repair point on the day; total chlorine should be >0.2 mg/L or not less than the reading taken just upstream of the repair point on the day). If the contractors procedure is not adequate then consider developing a simple water quality criteria that the contractor has to follow following repair works. | High | Utilities Engineer | 2024-06-01 |  | Completed
WQ 17 | Risk Register ID: R12 | Review documentation on process to inform/record new backflow prevention devices (BFD) in the BFD register when these are installed. | Low | Utilities Engineer with relevant PBPL staff | 2024-12-01 |  | Completed
WQ 18 | Risk Register ID: R12 | Investigate spreading the pressure monitoring across network (improvement in progress already). | Medium | Utilities Engineer with relevant PBPL staff | 2024-12-01 |  | Completed
WQ 19 | Risk Register ID: R16 | Investigate developing water quality modules and adding these to the corporate training matrix; or identifying relevant training which relevant staff require for their role in relation to the DWQMP and adding this to the training matrix. Consider 1) a general water quality awareness module for relevant staff, including all Managers/Executives. This will be around the DWQMP, obligations, improvement plan, integrated nature of maintaining water quality, how their roles may impact water quality; and 2) an operational-level specific training / micro-credential for awareness and responsibilities in relation to the DWQMP, monitoring result review and evaluation, incident response, DWQMP obligations, incident/event reporting to the regulator, etc. | Medium | Utilities Engineer | 2024-12-01 | 2025-12-01 | In Progress
WQ 20 | Risk Register ID: R17, R20 | Investigate adding resource (staff) to assist with implementing the DWQMP and provide contingency, especially with the proposed increase to the operational monitoring (weekly E. coli samples to be spread in the network, and turbidity, total chlorine, monochloramine, pH to be tested with the weekly E. coli testing. | High | Asset Services Manager | 2024-06-01 |  | Completed
WQ 21 | Risk Register ID: R20 | Investigate benefit of continuing with the in-house weekly testing or whether the weekly samples should also be collected and tested by an external laboratory. | High | Utilities Engineer with Asset Services Manager | 2023-12-01 |  | Completed
WQ 22 | Risk Register ID: R20 | Develop a standard operating procedure (SOP) on proper water sampling technique and testing in-house (if in-house testing is to be continued). Train the water samplers on use of this procedure. | High | Utilities Engineer | 2023-12-01 |  | Completed
WQ 23 | Risk Register ID: R20 | Investigate with IDEXX whether the water bath incubation is suitable or dry incubation (oven type incubator) is needed (if in-house testing is to be continued). | High | Utilities Engineer | 2023-12-01 |  | Completed
WQ 24 | Risk Register ID: R20 | Establish appropriate quality assurance / quality control (QA/QC) for the weekly in-house E. coli testing undertaken, including improved paper trail/record keeping etc (if in-house testing is to be continued). | High | Utilities Engineer | 2024-06-01 |  | Completed
WQ 25 | Risk Register ID: R20 | Investigate using the IDEXX Quanti-tray set up instead of presence/absence only as it can give counts for total coliforms and E. coli. Total coliform counts can provide early warning indication on need to flush system, start talks with UU, etc (if in-house testing is to be continued). | High | Utilities Engineer | 2023-12-01 |  | Completed
WQ 26 | Risk Register ID: R20 | Set up auto reminders for annual service/calibration of online chlorine analyser in PBPL system (e.g in TechOne when fully commissioned). | Low | Utilities Engineer | 2025-06-01 |  | Completed
WQ 27 | Risk Register ID: R24 | Investigate streamlining the process of recording all water quality related complaints into one system/place, which can make it easier to review, analyse and report on water quality complaints (in progress already). | Medium | Risk and Compliance Manager | 2024-12-01 |  | Completed
WQ 28 | Risk Register ID: R25 | Investigate periodic (e.g. 6-monthly or annual) water quality related information to be shared with customers (one-way information sharing) to remind them of their responsibility post the property meter. Information can also be on the PBPL website which in turn can link to websites like QLD Health. | Low | Utilities Engineer with Corporate Relations Manager | 2024-12-01 |  | Completed
WQ 29 | Risk Register ID: R25 | Review process of ship filling and water quality responsibility (i.e. relevant stakeholders should be aware of their obligations and that water quality can change post PBPL property meter with storage/detention etc). | Medium | Utilities Engineer | 2024-12-01 |  | Completed